# Model 2001-CSXX

# Power Monitor Module

# Operation Manual

Congratulations on your purchase, and welcome to Prodigit 2001-CSXX power monitor module. This operation manual will guide you step by step for the various functions of the Power Monitor.

Warning:

- To prevent fire or shock hazard, do not expose the unit to rain or moisture.

- The 2001-CS1X’s operating voltage is limited to 90~132Vrms 50/60Hz and the 2001-CS2X’s operating voltage is limited to 187~264Vrms 50/60Hz, Don't use it in other voltage ratings.

- Indoor use only.

- The maximum output current is 12/16/24A(This value can setting).The buzzer whistles and the reading on the LCD display flashes when over current.

- To avoid electrical shock, do not open the cabinet. Refer servicing to qualified personnel only.

- Installation: (Figure 1)

2001-CSXX include 8 precision digital Meter. Plug the 2001-CSXX to wall outlet, then connects the appliance or equipment to its receptacle, the LCD display will be lit after power up.

- The LCD shows all Volt, Current, Watt, Frequency, Power Factor, VA, KWH and elapsed time (hour) readings.

- Press the Volt key can select the volt mode on display.

- Press the Amp key can select the Amp mode on display.

- Press the Watt/VA key can select the Watt and VA mode on display.

- Press the HZ/PF key can select the Frequency and Power Factor value mode on display.

- Press the KWH can select the KWH and Elapsed time mode on display.

- Hole the Volt key 3 second can into Over Current Setting, the mode can select 15A/20A/30A Setting. The buzzer whistles when the current is over 15A/20A/30A * 80%.

MAINTENANCE

- Protect the meter from adverse weather conditions. The meter is not waterproof. Do not expose the LCD display to direct sunlight for long periods of time.

- CAUTION: To avoid damage to the meter, do not expose it to sprays, liquids, or solvents.

- Clean the exterior of the meter by removing dust with a lint-free cloth.

- Use care to avoid scratching the clear plastic display filter.

- For further cleaning, use a soft cloth or paper towel dampened with water. You can use a 75% isopropyl alcohol solution for more efficient cleaning.

- CAUTION: To avoid damage to the surface of the meter, do not use abrasive or chemical cleaning agents.

Specifications:

The Specification is base on sine wave & P.F.=1

| Model 2001-CSXX |
| --- |
| ITEM | 2001-CS1X | 2001-CS2X |
| RMS voltage | 90～132 Vrms | 187~264 Vrms |
| RMS current | 0.2～30.0 Arms | 0.2~30.0 Arms |
| Active power | 18～3960 Watts | 36~7920 Watt |
| Apparent power | 18～3960 VA | 36~7920 VA |
| Line Frequency | 47.0~63.0 Hz |
| Power Factor | 0.00～1.00 |
| KWH | 0.00～9999 KWH |
| Elapsed Time | 00:00～9999 |
| Accuracy |
| ITEM | Max. | Typ. |
| RMS voltage | 1% | 0.2% |
| RMS current | 1% | 0.3% |
| Active power | 2% | 0.5% |
| Apparent power | 2% | 0.5% |
| Line Frequency | 2% | ±0.1Hz |
| Power Factor | 0.03 | ±0.01 |
| KWH | 2% | 0.5% |
| Elapsed Time | 30 ppm |

Note:

1、The typical accuracy for voltage is in the range of 108V～132V(2001-CS1X, and for current is in the range of 0.2A～30A.

2、The typical accuracy for voltage is in the range of 187V～264V(2001-CS2X, and for current is in the range of 0.2A～30A.

Outward Size:

| Model | SIZE (L×W×H) |
| --- | --- |
| Model 2001-CSXH | 125mm×37.5mm×33mm |
| Model 2001-CSXV | 37.5mm×125mm×30mm |

Environment Condition:

- Altitude up to 2000m

- Operation temperature 5℃～40℃

- Max. R.H. 80%

- CAT Ⅱ

- Pollution degree 2

# Text boxes

Figure1:2001-CSXX Installation diagram

Figure 2 ：Type Description diagram

Figure 3 ：2001-CSXX Wiring Diagram

Figure 1：2001-CSXX surface diagram